TECHNICAL DATA LEAFLET GAS

Riello 40 FSD Series Two Stage Gas Burners

FS5D 12/23 ÷ 58 kW

FS20D 58/81 ÷ 220 kW

www.riello.com

Two Stage Gas Burners FSD 5 ÷ 20 Series

The Riello 40 FSD series of one stage gas burners, is a complete range of products developed to respond to any request for light
industrial application. The Riello 40 FSD series is available in five different models, with an output ranging from 11 to 220 kW,
divided in four different structures.

All the models use the same components designed by Riello for the Riello 40 FSD series. The high quality level guarantees safe
working.

The Riello 40 FSD burners are fitted with a microprocessor - based control box, with diagnostic functions.

In developing these burners, special attention was paid to reducing noise, to the ease of installation and adjustment, to

obtaining the smallest size possible to fit into any sort of boiler available on the market. All the models are approved by the EN
676 European Standard and conform to European Directives for EMC, Low Voltage, Machinery and Boiler Efficiency.
All the Riello 40 FSD burners are tested before leaving the factory.

2

Technical Data

MODEL FS5D FS20D

Burner operation mode Two stage
Modulation ratio at max. output ===
Servomotor type R.B.L BERGER
 run time s 12/23 ÷ 58 58/81 ÷220

Heat output kW 10/20 ÷ 50 50/70 ÷ 189
 Mcal/h 9.5 ÷ 30 20 ÷ 50

Working temperature °C min./max. 0/40
FUEL/AIR DATA

G20 gas net calorific value kWh/Nm3 10
 gas density kg/Nm3 0.71

gas delivery Nm3/h 1.2/2.3 ÷ 5.8 5.8/8.1 ÷ 22
G25 gas net calorific value kWh/Nm3 8.6
 gas density kg/Nm3 0.78

gas delivery Nm3/h 1.4/2.7 ÷ 6.7 6.7/9.4 ÷ 25.6
LPG gas net calorific value kWh/Nm3 25.8
 gas density kg/Nm3 2.02

gas delivery Nm3/h 0.4/0.8 ÷ 2.2 2.2/3.1 ÷ 8.5
Fan type Centrifugal with forward curve blades
Air temperature max °C 40
ELECTRICAL DATA

Electrical supply Ph/Hz/V 1/50/230 (±10%)
Auxiliary electrical supply Ph/Hz/V ===
Control box type MG 557/3 RMG 88.62C2
Total electrical power kW 0.110 0.250
Auxiliary electrical power kW ===
Protection level IP X0D
 Fan motor electrical power kW 0.09 0.15
 rated current A 0.65 1.4

start up current A 2.6 5.6

protection level IP 20

Ignition transformer type Incorporated in the Separated from the
 control box control box

V1 - V2 (-) - 8 kV 230 V - 8kV

I1 - I2 (-) - 12 mA 1.8 A - 30 mA  Operation Intermittent (at least one stop every 24 h)
EMISSIONS

Noise levels sound pressure dB (A) 60 73
 sound power W ===

Gas G20 CO emission mg/kWh < 40

NOx emission mg/kWh ≤ 120 APPROVAL

Directive 2006/42/EC - 2009/142/EC - 2014/30/UE - 2014/35/UE
Conforming to EN 676 - EN 12100
Certification CE-0694CN7805

Reference conditions:

Temperature: 20°C - Pressure: 1013.5 mbar - Altitude: 0 m a.s.l. - Noise measured at a distance of 1 meter.

Since the Company is constantly engaged in the production improvement, the aesthetic and dimensional featu-
res, the technical data, the equipment and the accessories can be changed. This document contains confidential
and proprietary information of RIELLO S.p.A. Unless authorised, this information shall not be divulged, nor du-
plicated in whole or in part.

3

Two Stage Gas Burners FSD 5 ÷ 20 Series

Firing Rates

Useful working field for choosing the burner

1st stage operation range

Test conditions
conforming to EN676
Temperature: 20°C
Pressure: 1013.5
mbar Altitude: 0 m
a.s.l.

4

Gas train

GAS TRAIN DESIGNATION

Series: MB

MBC

Size: 405 407 410

65

Operation: /1 stage mode opening

/2 two stage mode opening

Leak detection control: - 0

Joint type: R threaded joint

F1 square flange BS1

F2 square flange BS2

F3 square flange BS3 - BS4

Electrical connection: SD Domestic plug

T Terminals - Terminal strip

|  | Standard output pressure range: |  | - without pressure governor |
| --- | --- | --- | --- |

0 with governor and air/gas proportional pressure

2 with governor and output pressure up to 20 mbar

3 with governor and output pressure up to 30 mbar

4 with governor and output pressure up to 40 mbar

5 with governor and output pressure up to 50 mbar

Valve control: 0 shared

MB 407 /2 - R SD 2 0

BASIC DESIGNATION

EXTENDED DESIGNATION

5

Two Stage Gas Burners FSD 5 ÷ 20 Series

GAS TRAINS

The burners are set for gas supply from either the right or left hand sides.

Depending on the fuel output and the available pressure in the supply line, you should check the correct gas
train to be adapted to the system requirements. The gas train is Multibloc type, containing the main components
in a single unit and it can be fitted with the valves seal control (as accessory).

MB 405-407-410

L1 L 1 Gas input pipework

|  | 2 1 3 |  |  |  |  | 4 |  |  |  |  | P2 |  |  |  | 5 |  | 6 |  |  |  | MULTIBLOC 7 9 8 |  |  |  |  |  |  | P1 |  |  |  | 2 Manual valve (charged to the in- staller) 3 Antivibrating joint 4 Gas pressure gauge 5 Gas filter |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  | 10 |  | LEAK DETECTION CONTROL DEVICE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 11 |  |  |  | 12 |  | 6 Min. gas pressure switch 7 Safety gas valve 8 Adjustment solenoid: 1st and 2nd stage:firing delivery adjustment (rapid opening) maximum delivery adjustment (slow opening) 9 Pressure regulator 10 Leak detection control device for val- ves 7 and 8 (accessory) 11 Gas train-burner adapter 12 Burner 13 Shutter with adjustment screws 14 Pressure regulator setting device 15 Regulation solenoid P1 Combustion head pressure P2 Upstream pressure from the filter P3 Upstream pressure from the control valve |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Y |  |  |  |  |  |  |  |  |  | L Gas train supplied separately L1 Installer’s responsability |
|  |  | Z |  | Øi |  |  |  |  |  |  |  |  | X |  |  |  |  |  | W |  |  |  |  | The dimensions of the gas trains vary depending on their construction features. The following table shows the dimensions of the gas trains that can be fitted to Riello 40 FSD burners, intake and outlet diameters. |  |  |  |  |  |  |  |  |  |  |  |

GAS TRAIN

MODEL CODE Ø in Ø out X mm Y mm W mm Z mm
MB 405/2 3970084 Rp 1/2” Rp 1/2”(*) 321 257 46 120
MB 407/2 3970537 Rp 3/4” Rp 3/4” 371 257 46 120
MB 410/2 3970534 1” Rp 3/4” 405 315 55 145

(*) With 1/2” - 3/4” reduction nipple supplied.

6

Pressure Drop Diagram

The diagrams indicate the minimum pressure drop of the burners with the various gas trains that can be matched
with them; at the value of these pressure drop add the combustion chamber pressure.

The value thus calculated represents the minimum required input pressure to the gas train.

FS5D (NATURAL GAS)

G20 G25

14

20

MBC 65/2

12 MBC 65/2

15
10

MB 405/2
 MB 405/2

8

|  | 6 |  | MB 407/2 MB 410/2 |  | 10 |  | MB 407/2 MB 410/2 |
| --- | --- | --- | --- | --- | --- | --- | --- |

4
 5

2

|  | 0 |  | 18 58 20 30 40 50 kW |  | 0 |  | 18 58 20 30 40 50 kW |
| --- | --- | --- | --- | --- | --- | --- | --- |

FS5D (LPG)

G31
12

MBC 65/2 10

8

MB 405/2

6

4

2

|  | 0 |  | 18 58 20 30 40 50 kW |
| --- | --- | --- | --- |

For pressure levels different from those indicated above, please contact Riello Burners Technical Office.
In LPG plants, Multibloc gas trains do not operate below 0°C.

They are only suitable for gaseous LPG (liquid hydrocarbons destroy the seal materials).

Combustion head + gas train
Combustion head

7

Two Stage Gas Burners FSD 5 ÷ 20 Series

FS20D (NATURAL GAS)

G20 G25
 45

30

40

25

MB 407/2 MB 407/2
 35

30
20

25

15 MB 410/2 MB 410/2
 20

15
10

10

5

5

|  | 0 |  | 81 220 100 125 150 175 200 kW |  | 0 |  | 81 220 100 125 150 175 200 kW |
| --- | --- | --- | --- | --- | --- | --- | --- |

FS20D (LPG)

G31

25

MB 407/2
20

MB 410/2 15

10

5

|  | 0 |  | 81 220 100 125 150 175 200 kW |
| --- | --- | --- | --- |

For pressure levels different from those indicated above, please contact Riello Burners Technical Office.
In LPG plants, Multibloc gas trains do not operate below 0°C.

They are only suitable for gaseous LPG (liquid hydrocarbons destroy the seal materials).

Combustion head + gas train
Combustion head

8

Ventilation

The different ventilation circuits always ensure low noise levels with high performance of pressure and air
delivery, inspite of their compact size.

The burners are fitted with an adjustable air pressure switch, conforming to EN 676 standards.

Air suction

Combustion Head

The combustion head in Riello 40 FSD burners is the result of an innovative design, which allows combustion
with low polluting emissions, while being easy to adapt to all the various types of boilers and combustion
chambers.

Simple adjustment allows
the internal geometry of
the combustion head to
be adapted to the burner
output.

Combustion head Mobile flange

DIMENSIONS OF THE FLAME

2

|  |  |  | L max |  |  |  | 1 |  | D |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 1 |  |  | L min |

max

L 0,5

|  | 0 0 0 100 200 300 400 500 Burner output (kW) |  | Example: Burner thermal output = 350 kW; L flame (m) = 1.2 m (medium value); D flame (m) = 0.6 m (medium value) |
| --- | --- | --- | --- |

9

Two Stage Gas Burners FSD 5 ÷ 20 Series

Operation

| All these models are two stage operation. |  | °C bar 1st |  |  |
| --- | --- | --- | --- | --- |
| The Riello 40 FSD series of two stage burners allows operating at both full and reduced output, with consequent reduction in turning the burner on and off, their giving better performance to the boiler. |  |  |  | 2st |  |  |  | ON ON |  |  | time |  |
| During stand-by, the air damper is completely closed (controlled by an electric servomotor) and prevents heat loss due to the flue draught. |  |  |  |  |  |  | OFF OFF |  |  |  |  | time |  |

Two stage operation Air damper adjustment

The FS5D model is fitted with the new MG 557 microprocessor control panel. For helping the commissioning and
maintenance work, there are two main elements:

|  | Switch |  | The lock-out reset button is the central operating element for resetting the burner control and for activating / deactivating the diagnostic functions. |
| --- | --- | --- | --- |

The multi-color LED is the central indication element for visual diagnosis and interface diagnosis.

Both elements are located under the transparent cover of lock-out reset button, as showed below.

Switch

10

There are two diagnostic choices, for indication of operation and diagnosis of fault cause:

- visual diagnosis:

- interface diagnosis:

By the interface adapter and a
PC with dedicated software.

INTERFACE ADAPTER

COMPUTER

Indication of operation:

In normal operation, the various statues are indicated in the form of colour codes according to the table below.

Color code table

Operation status Color code Stand-by Led off

Pre-purging Green

Ignition phase Green

Flame OK Green

Post purge Green

Undervoltage, built-in fuse Led off

Fault, alarm Red

Flame simulation Led off

11

Two Stage Gas Burners FSD 5 ÷ 20 Series

Diagnosis of fault causes:

After lock-out has occurred, the red signal lamp is steady on. In this status, the visual fault diagnosis according
to the error code table can be activated by pressing the lock-out reset button for > 3 seconds.

The interface diagnosis (with adapter) can be activated by pressing again the lock-out button for > 3 seconds.

Example of blinks sequence:

|  | Press reset for 3s Interval 2s |  | LED off RED LED illuminated LED flashes |
| --- | --- | --- | --- |

Error code table

Signal Possible cause

| 2 flashes |  | The flame does not stabilise at the end of the safety time: - faulty ionisation probe - faulty or soiled gas valves - neutral/phase exchange - faulty ignition transformer - poor burner regulation (insufficient gas) |
| --- | --- | --- |
| 3 flashes |  | Min. air pressure switch does not close or is already closed before the limit thermostat closed: - air pressure switch faulty - air pressure switch incorrectly regulated |  |

4 flashes Presence of flame:
 - in stand-by position after heat demand

- during pre-purging

6 flashes Loss air pressure:
 - during pre-purging

- during safety time or operations

| 7 flashes |  | Loss of flame 4 times during operations after 3 attempts of re-cycle: - poor burner regulation (insufficient gas) - faulty or soiled gas valves - short circuit between ionisation probe and earth - faulty ionisation probe |
| --- | --- | --- |

12

The FS20D model is fitted with the new microprocessor control panel for the supervision during intermittent
operation.

For helping the commissioning and maintenance work, there are two main elements:

|  | Switch |  | The lock-out reset button is the central operating element for resetting the burner control and for activating / deactivating the diagnostic functions. |
| --- | --- | --- | --- |

The multi-color LED is the central indication element for visual diagnosis and interface diagnosis.

Both elements are located under the transparent cover of lock-out reset button, as showed below.

Switch

There are two diagnostic choices, for indication of operation and diagnosis of fault cause:

- visual diagnosis:

- interface diagnosis:

|  | INTERFACE ADAPTER |  | By the interface adapter and a PC with dedicated software or by a predisposed flue gas analyzer (see paragraph accessories). |
| --- | --- | --- | --- |

COMPUTER

FLUE GAS
ANALYSER

13

Two Stage Gas Burners FSD 5 ÷ 20 Series

Indication of operation:

In normal operation, the various status are indicated in the form of colour codes according to the table below.
The interface diagnosis (with adapter) can be activated by pressing the lock-out button for > 3 seconds.

Color code table

Operation status Color code Stand-by

Pre-purging

Ignition phase

Flame OK

Poor flame

Undervoltage, built-in fuse

Fault, alarm

Extraneous light

LED off

Diagnosis of fault causes:

After lock-out has occurred, the red signal lamp is steady on. In this status, the visual fault diagnosis according
to the error code table can be activated by pressing the lock-out reset button for > 3 seconds.
The interface diagnosis (with adapter) can be activated by pressing again the lock-out button for > 3 seconds.
The flashes of red LED are a signal with this sequence :

(e.g. signal with n° 3 ﬂashes – faulty air pressure monitor)

LED off

3 sec. 3 sec. 3 sec.

Error code table

Flash code Possible cause of fault

| 2 flashes |  | No establishment of flame at the end of safety time : - faulty or soiled fuel valves - faulty or soiled flame detector - poor adjustment of burner, no fuel - faulty ignition equipment |
| --- | --- | --- |

3 flashes

Faulty air pressure monitor

4 flashes

Simulation of flame on burner start up

| 7 flashes |  | Loss of flame during operation : - faulty or soiled fuel valves - faulty or soiled flame detector - poor adjustment of burner |
| --- | --- | --- |

10 flashes

Wiring error or internal fault

14

START UP CYCLE

Regular operation FS5D

P

KEY TL

t2

t1 I Ignition transformer

t3

|  | M I V1 V2 |  | M |  | t4i ts |  | t5 |  | LED Reset button LED indicating operating status M Fan motor SO Ionisation probe TL Limit thermostat V1 1st stage gas valve. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

V2 2nd stage gas valve

SO

Red (LED signalling)
Green

Green (LED signalling)
LED

|  | Flame loss during operation (Recycle max. 3 attempts) MV = idle |  | No signal needs to be received |
| --- | --- | --- | --- |

t4L

Lo. ckout

SO

Green

LED

Lockout due to ignition failure FS5D

P TL

t2

t1 t3

M M
 t4i

I

ts

V1

Red (LED signalling)

Green (LED signalling)
V2

|  | SO |  | Lockout KEY . I Ignition transformer LED Reset button LED indicating operating status |
| --- | --- | --- | --- |

M Fan motor Green Red

|  | LED |  | SO Ionisation probe TL Limit thermostat |
| --- | --- | --- | --- |

V1 1st stage gas valve

V2 2nd stage gas valve

Operating times (in seconds)

t1, t3l, t4l, t4a t2l t2, t4i t2a t3 t3a t3r ts t5 t6

max max - - - max max - min/max max

1 30 3 120 40 15 70 3 5/25 360

15

Two Stage Gas Burners FSD 5 ÷ 20 Series

Lockout due to a flame or flame simulation FS5D detected during pre-purging

P TL

|  | t2 |  | t1 t3 |
| --- | --- | --- | --- |

M M

I

ts

V1

Red (LED signalling)

V2

Green (LED signalling)

|  | SO |  | Green |  | Lockout . Red |  | KEY I Ignition transformer |
| --- | --- | --- | --- | --- | --- | --- | --- |

LED

LED Reset button LED indicating operating status

M Fan motor

SO Ionisation probe

TL Limit thermostat

V1 1st stage gas valve

V2 2nd stage gas valve

t1, t3l, t4l, t4a t2l t2, t4i t2a t3 t3a t3r ts t5 t6

max max - - - max max - min/max max

1 30 3 120 40 15 70 3 5/25 360

Lockout due to ignition failure FS20D

Normal Lockout due to ignition failure

TL

M

I

V1

F1

V2

F2

LO

max. 3s

max. 2s 40s 10s max. 2s 40s max. 3s

KEY

I Ignition transformer

F1 1st stage flame

F2 2nd stage flame

LO Lockout

M Fan motor

TL Limit thermostat

V1 1st stage gas valve

V2 2nd stage gas valve

16

Emissions

The emission data have been measured in the various model at maximum output, in conformity with EN 676 standard.

NOx EMISSIONS

120

110

100

90

80

70

60 FS5D FS20D

50

CO EMISSIONS

35

30

25

20

15

FS5D FS20D

10

NOISE EMISSIONS

80

76

72

68

64

60

56 FS5D FS20D

52

Special attention has been paid to noise reduction.

All models are fitted with sound-proofing material inside the cover.

17

Two Stage Gas Burners FSD 5 ÷ 20 Series

Overall Dimensions (mm)

These models are distinguished by their reduced size, in relation to the outputs achieved, which means they can
be fitted to any boiler on the market.

BURNER

MODEL A C D E F H I N V Z

FS5D 306 170 233 295 100 91 180 48 138 28

FS20D 413 238 298 389 120 125 230 67 152 33

BURNER - BOILER MOUNTING FLANGE

FS5D FS20D

MODEL A1 A2 B1 B2 C C1 F Q R

FS5D - - - - 140 130 170 45° 10

FS20D 155 200 155 200 170 - 170 90° 11

PACKAGING

Z

MODEL X Y Z kg

|  | X |  | Y |  | FS5D 445 355 325 10 FS20D 535 535 375 20 |
| --- | --- | --- | --- | --- | --- |

18

Installation Description

Installation, start up and maintenance must be carried out by qualified and skilled personnel.
The burner is set in factory on standard calibration (minimum output), if necessary adjustments can be made on
the basis of the maximum output of the boiler.

All operations must be performed as described in the technical handbook supplied with the burner.

BURNER SETTING

The air damper position is easy to set, and in the FS20D can
be adjusted without removing the burner cover.

Head setting is easy and aided by a graduated scale, a test
point allows reading the air pressure in the combustion
head.

Riello 40 FSD burners are fitted with an air pressure switch
which, in accordance with EN 676 standards, can be
adjusted by the installer using a graduated selector, on the
basis of the effective working conditions.

MAINTENANCE

The maintenance position is easily carried out by hinge that
joins the body of burner to the flange.

19

Two Stage Gas Burners FSD 5 ÷ 20 Series

Burner accessories

REMOTE RESET CONTROL KIT FOR THE MG 557/3 CONTROL BOX

The MG 557 control box can be remotely released using an electric command kit.
This kit must be installed in conformity with the local authority.

BURNER CODE

FS5D 3002750

EXTENDED HEAD KIT

“Standard head” burners can be transformed into “extended head” versions by
using the special kit. Below the KITS available for the various burners are listed,
showing the original and the extended lengths.

|  | BURNER |  | STANDARD HEAD LENGTH (mm) |  | EXTENDED HEAD LENGTH (mm) |  | CODE |
| --- | --- | --- | --- | --- | --- | --- | --- |

FS5D 100 125 3000820

FS20D 120 280 3000873

LPG KIT

For burning LPG gas, a special kit is available to be fitted to the combustion head
on the burner, as shown in the following table.

|  | BURNER |  | STANDARD HEAD CODE |  | EXTENDED HEAD CODE |
| --- | --- | --- | --- | --- | --- |

FS5D 3000882 3000882

FS20D 3000886 3000886

TOWN GAS KIT

BURNER KIT CODE

FS5D 3000889

FS20D 3000894

7-PIN PLUG KIT

If necessary a 7-pin plug kit is available (in packaging of n. 5 pieces).

BURNER CODE

FS5D - FS20D 3000945

20

END CONE WITH TURBULATOR DISK

The end cone turbolator disk reduces the flame lenght. It is suitable for hoven
application (CO emissions) and short boiler chamber.

BURNER PROJECTION (mm) CODE

FS5D +15 3000916

FS20D +23 3000919

CONTINUOUS VENTILATION KIT FOR RMG CONTROL BOX

If the burner requires continuous ventilation in the stages without flame, a spe-
cial kit is available as given in the following table.

BURNER CODE

FS20D 3010094

PC INTERFACE KIT

To connect the control box to a personal computer for the transmission of opera-
tion, fault signals and detailed service information, an interface adapter with PC
software are available.

BURNER KIT CODE

FS5D 3002731

FS20D 3002719

Gas train accessories

SEAL CONTROL KIT

To test the valve seals on the gas train a special “seal control kit” is available.

|  | GAS TRAIN |  | CODE for 50Hz operation |  | CODE for 60Hz operation |
| --- | --- | --- | --- | --- | --- |

MB/1 type 3010123 20050030

21

Two Stage Gas Burners FSD 5 ÷ 20 Series

Specification

DESIGNATION OF SERIES

A specific index guides your choice of burner from the various models available in the BS series. Below is a clear
and detailed specification description of the product.

Series: F

Fuel: S Natural Gas

Size:

Optional variations: D Two - stage output adjustment

Electrical supply to the system: 1/230/50 1/230V/50Hz

F S 5 D 1/230/50

BASIC DESIGNATION

EXTENDED DESIGNATION

AVAILABLE BURNER MODELS

| BURNER MODELS ELECTRICAL SUPPLY |  | HEAT OUTPUT TOTAL ELECTRICAL POWER (kW) (kW) NATURAL GAS (Nm3/h) |  | CERTIFICATION NOTE |
| --- | --- | --- | --- | --- |

FS5D 1/230/50 12/23 - 58 1.2/2.3 - 5.8 0.110 CE–0694 CN7805 (1)

FS20D 1/230/50 58/81 - 220 5.8/8.1 - 22 0.250 CE–0694 CN7805 (1)

Net calorific value G20: 10 kWh/Nm3 - Density: 0.71 kg/Nm3
The burners of FSD series are in according to EN 676
(1) With terminal block.

22

SPECIFICATION

STATE OF SUPPLY

Burner

Monoblock, gas burners, completely automatic, with two stage settings fitted with:
- Fan with forward curve blades

- Metallic cover

- Air damper, open in stand by, driven by an electric servomotor
- Air damper with 1st and 2nd stage adjustement
- Single phase electric motor 230 V, 50 Hz

- Combustion head fitted with:

- stainless steel head cone, resistant to high temperatures
- ignition electrodes

- ionisation probe - gas distributor

- flame stability disk

- Adjustable air pressure switch, with graduated selector, to guarantee burner lock out in the case of
 insufficient combustible air

- Microprocessor-based burner safety control box MG 557 (with diagnostic, remote reset, continuous purge
 integrated, recycle, post-purge)

- IP X0D (IP 40) electric protection level.

Stndard equipment: - Insulating gasket

- Screws and nuts for fixing the flange to the boiler
- Hinge

- Cable grommet

- Instruction handbook for installation, use and maintenance
- Spare parts catalogue.

Conforming to:

- 2014/30 UE Directive (electromagnetic compatibility)
- 2014/35 UE Directive (low voltage)

- 2009/142 EC Directive (gas)

- 2006/42 EC Directive (machine)
- EN 676 (gas burners)

Available accessories to be ordered separately:
- Remote reset control kit for MG 557/3 control box
- Extended head kit

- LPG kit

- Town gas kit

- 7-pin plug kit

- End cone with turbulator disk
- Continuous ventilation kit for RMG control box
- PC interface kit - Seal control kit

23

Riello Burners a world of experience in every burner we sell.

Across the world, Riello sets the standard in reliable and

high efficiency burner technology.

With burner capacity from 5 kW to 48 MW, Riello gas,

oil, dual fuel and Low Nox burners deliver unbeatable

performance across the full range of residential and

commercial heating applications, as well as in industrial

processes.

With headquarter in Legnago, Italy, Riello has been

manufacturing premium quality burners for over 90 year.

The manufacturing plant is equipped with the most

innovative systems of assembling lines and modern

manufacturing cells for a quick and flexible response to

the market.
[ 1 ]

Besides, the Riello Combustion Research Centre, located in

Angiari, Italy, represents one of the most modern facility

in Europe and one of the most advanced in the world for

the development of the combustion technology.

Today, the company’s presence on worldwide markets is

distinguished by a well-constructed and efficient sales

network, alongside many important Training Centres

located in various countries to meet its customers’ needs.

Riello has 13 operational branches abroad (in Europe,

America and Asia), with customers in over 60 countries.

[ 2 ]

| [ 1 ] |  |  | BURNERS PRODUCTION PLANT S. PIETRO, LEGNAGO (VERONA) - ITALIA |  |
| --- | --- | --- | --- | --- |
| [ 2 ] |  |  |  | HEADQUARTER BURNERS DIVISION S. PIETRO, LEGNAGO (VERONA) - ITALIA |  |

RIELLO S.p.A. - 37045 Legnago (VR) - Italy

tel. +39 0442 630111 - fax: +39 0442 21980

www.riello.com

Since the Company is constantly engaged in the production improvement, the aesthetic
and dimensional features, the technical data, the equipment and the accessories can be
changed. This document contains confidential and proprietary information of RIELLO S.p.A.
Unless authorised, this information shall not be divulged, nor duplicated in whole or in part.